HOT WORK PERMIT

| Date of Issue |  |  |  |  | Valid from / to |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| - WORKER DETAILS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Hot Work undertaken by |  |  |  |  | Phone Number |  |  |  |  |  |  |  |  |
| - PROJECT / WORKS DETAILS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Location of work |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Planned work activity |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - ISOLATIONS REQUIRED |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Essential Services (gas, water, electricity) |  |  | Fire Indicator Panel |  |  |  |  |  | Fire Supression Systems |  |  |
| - GENERAL WORK CONTROLS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Controls (Identify those general Hot Work & Ignition controls to be undertaken as part of the Hot Work) |  |  |  |  |  |  |  |  |  |  | Yes | NA |  |
| Fire extinguishers supplied by are to be located immediately adjacent to the Hot Work area and within fifteen (15) metre of the work to be carried out |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Position Catch mats or boards over grid-mesh, flooring, or grates to catch sparks, slag, or other hot debris. Spark and flash screens are in place. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Drains, cable racks, electrical cables and other heat/fire sensitive items are covered |  |  |  |  |  |  |  |  |  |  |  |  |  |
| If working outdoors, the area has been wetted down prior to work commencing and water is available and onsite if required. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| One (1) metre clearance to any insulated sandwich panel (otherwise relocate work or provide thermal barrier). |  |  |  |  |  |  |  |  |  |  |  |  |  |
| A four (4) metre cleared space around and above the area where Hot Work is to be performed. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The worksite has been isolated and traffic/pedestrian movement restricted. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Is the wind direction satisfactory for Hot Work to be done |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Is Hot Work Activity located at a level which has the potential for a fall hazard (Working at Heights Permit to be used in conjunction with Hot Work Permit) |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - COMPLETION SIGN OFF |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fire Watch |  | A continuous fire watch must be provided during and for a minimum of 30 minutes after work, after which periodic checks are required for a further 60 minutes (with checks undertaken every 10-15 minutes). |  |  |  |  |  |  |  |  |  |  |  |
| Name |  |  |  |  |  | Signature |  |  |  |  |  |  |  |
| Completion date / time |  |  |  |  |  |  |  |  |  |  |  |  |  |