EMERGENCY SHOWER / EYEWASH ANNUAL TEST

| Annual Testing Requirements |  | Unit 1 | Unit 2 | Unit 3 | Unit 4 |
| --- | --- | --- | --- | --- | --- |
| Testing tag is connected to unit and up to date |  |  |  |  |  |
| Flushing fluid is at room temperature (between 15o and 35oC) |  |  |  |  |  |
| Shower and eye wash control valve remains open |  |  |  |  |  |
| Eyewash dust covers are fitted and open automatically on operation |  |  |  |  |  |
| Passed eyewash gauge test |  |  |  |  |  |
| Minimum eyewash flow rate 1.5L minute at 210kPa |  |  |  |  |  |
| Minimum shower flow rate 75.7L minute at 210kPa |  |  |  |  |  |
| Flow of water starts within one (1) second |  |  |  |  |  |
| Signage is legible and clearly displayed |  |  |  |  |  |
| Comments / Notes: |  |  |  |  |  |
| Building: |  |  |  |  |  |
| Room: |  |  |  |  |  |
| Tested by: |  |  |  |  |  |
| Date: |  |  |  |  |  |